# DDC Zone Thermostat Controller

# Division 23 – Heating, Ventilating, and Air Conditioning

# Section 23 09 00 – Instrumentation and Control for HVAC

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

# PART 1 – GENERAL

## Section Includes

- DDC Zone Thermostat Controller.

## Related Requirements

- Section 01 40 00 - Quality Requirements

- Section 01 78 00 - Closeout Submittals

- Section 01 79 00 - Demonstration and Training

## Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

BACnet International – Building Automation and Control networks: communications protocol for building automation control networks that leverage the ASHRAE, ANSI and ISO standard protocols.

- ANSI/ASHRAE Standard 135.1 – Method of Test for Conformance to BACnet.

- ISO 16484-5 – Building Automation and Control Systems: Data communication protocol.

BTL – BACnet Testing Laboratories.

## Documentation

- The manufacturer shall provide documentation for each device to address typical wiring, sequence of operation, physical dimensions of components and installation procedures and requirements.

## Quality Assurance

- The manufacturer qualifications shall be specified in this section, with minimum ten years of documented experience.

## Warranty

- The warranty shall begin upon the date of shipment and continue for a period of 18 months.

  - The warranty shall cover all products from manufacturer defect and shall include any replacement parts only during the coverage period.

  - The manufacturer shall not include the cost of labor to replace or recalibrate, if necessary, any components found to be defective.

  - This warranty does not cover any product failure which results from, either directly or indirectly, any damage which occurs to the device by improper installation or from failure to comply with the preventative maintenance required per the manufacturer’s instructions, or by codes set by local or facility authorities.

  - An extended warranty shall be available at additional cost from the manufacturer.

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

# PART 2 – PRODUCTS

## 2.01	VAV Zone Controllers

- Basis of Design:  Price Industries, Inc.

- DDC Zone Thermostat Controller:  Model Disio Display

## Disio Display Thermostat Controller

- Description:

    - DDC Zone Thermostat Controller shall be integral, wall mounted design without the need for a separate circuit board for inputs and outputs.

    - DDC Zone Thermostat Controller shall include 4 fully configurable universal outputs from the control board utilizing a PI control loop to control a VVT damper actuator, electric reheat, and cold/hot water coils for the purpose of maintaining a user defined space temperature.

    - DDC Zone Thermostat Controller shall include 4 fully configurable universal inputs capable of taking in 0-10VDC signals, binary 24 VAC signals, binary contact closure input, or 10 K ohm thermistors.

    - The DDC Zone Thermostat Controller shall be digital and utilize a microcontroller with EEPROM for storing setup and calibration variables. Screen shall utilize a 2 character, 7 segment display for setpoint and display information.

    - The controller package shall measure zone temperature and shall feature local set-point adjustment with adjustable lockout ranges.

    - The DDC Zone Thermostat Controller shall feature an easy-to-read screen which is angled up at the user when mounted on the wall for a more optimal viewing angle, thermostats with a screen parallel to the wall shall not be accepted.

    - Screen shall be solid piece of glass with capacitive touch buttons, thermostats with push buttons protruding from the face of the thermostat shall not be accepted.

    - Thermostat shall have integral thermistor for accurate room air temperature measurement. Temperature measurement circuit shall include provision to specifically avoid self-heating to prevent temperature measurement error.

Electrical:

- Controller shall be factory programmed with a sequence of operations and can be re-programmed with different sequences on site.

Interfacing to EMS/BMS/BAS:

- The VAV Zone Controller shall interface with the building management system (BMS) to allow remote monitoring of room parameters or permit settings adjustments over the building network.

- BMS shall use BACnet MS/TP network protocol to viewpoints or status of room space. The use of BACnet protocol shall be native to the device and shall not require the use of an external gateway.

- Thermostat shall include ability to change MAC address, device instance and baud rates (9600, 19200, 38400, 76800) for proper interfacing to BACnet network.

- Device shall support on board network termination for the MS/TP network.

- The VAV Zone Controller shall be BTL listed.

- Manufacturer shall be a member of BACnet International.

- BACnet points shall include – Device Object, Analog Input (AI), Analog Output (AO), Binary Input (BI), Binary Output (BO), Multi-state (MSV). All temperature set points and minimum and maximum damper positions shall be adjustable from the BACnet network.

# PART 3 – EXECUTION

## 3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

## 3.02	Installation

- The mechanical contractor, controls contractor, or factory authorized commissioning contractor shall install and wire the components of the VAV zone controller. This shall include the thermostat, airflow control devices, and all network wires.

- The VAV zone controller shall have the following cable and wire requirements

- Network wiring shall be 3 wire connection consisting of 2 - low capacitance (17 pF or less) plenum rated, balanced twisted pairs.

- All cables/wires to be provided by installing contractor.

## 3.03	Start-Up and Commissioning

- Start-up shall include verifying proper installation, testing and airflow control, setting all parameters and set points, and configuring and verifying network communication, as applicable.

- The test and balance (TAB) contractor shall be responsible for final verification of airflow measurement.

## 3.04	Field Quality Control

- See Section 01 40 00 - Quality Requirements, for additional quality requirements.

## 3.05	Closeout Activities

- The manufacturer or manufacturer’s representative shall provide a minimum of four hours of owner training to facilities personnel or other parties as required.

- See Section 01 79 00 - Demonstration and Training for additional closeout requirements.

END OF SECTION