**Price ATG/STG Transfer/Door Grille**

**Division 23 – Heating, Ventilating, and Air Conditioning**

**Section 23 37 13 – Diffusers, Registers, and Grilles**

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

**PART 1 – GENERAL**

* 1. **Section includes**:

1. Sight-proof Transfer/Door Grille.
   1. **Related Requirements**
2. Section 01 30 00 – Administrative Requirements
3. Section 01 40 00 – Quality Requirements
4. Section 01 60 00 – Product Requirements
5. Section 01 74 21 – Construction/Demolition Waste Management and Disposal
6. Section 01 78 00 – Closeout Submittals
7. Section 01 79 00 – Demonstration and Training
   1. **Reference Standards**
8. All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.
9. ASHRAE 70 – Method of Testing the Performance of Air Outlets and Air Inlets
10. ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces
11. ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints
12. ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes
13. ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments
14. ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

**1.04 Submittals**

A. See Section 01 30 00 – Administrative Requirements for submittal procedures.

B. Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, static pressure, and NC designation.

C. Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

F. Project Record Documents: Record actual locations of units and control components.

G. Operation and Maintenance Data: Include manufacturer's descriptive literature, operating instructions, maintenance and repair data, and parts lists.

H. Warranty: Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

I. Maintenance Materials: Furnish the following for Owner's use in maintenance of project.

* 1. See Section 01 60 00 - Product Requirements for additional provisions.

**1.06 Quality Assurance**

1. Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

**1.07 Warranty**

1. See Section 01 7800 - Closeout Submittals, for additional warranty requirements.
2. Provide 12 month manufacturer warranty from date of shipment of grilles.

**PART 2 – PRODUCTS**

**2.01 Sight-proof Transfer/Door Grilles**

1. Basis of Design: Price Industries, Inc.
   1. Sight-proof Transfer/Door Grilles – Steel Construction: Model STG1
   2. Sight-proof Transfer/Door Grilles – Aluminum Construction: Model ATG1/ATGH
   3. Sight-proof or Light-proof Transfer/Door Grilles – Aluminum Construction: Model ATG2
2. General:
   1. The transfer/door grille shall be supplied with a sight-proof core to allow airflow to a space that is not directly served by a ducted source of supply air or a ducted outlet for return or exhaust.
3. Sight-Proof Transfer/Door Grilles – Steel Construction [Price Model STG1]:
   1. Construction
      1. Core and frame material shall be steel.
   2. Finish shall be (**select one**):
   3. Paint finish shall be (**select one**):
      1. Baked-on powder coat finish.
         1. The paint film thickness shall be a minimum of 2 mils.
         2. The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.
         3. The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.
         4. The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.
         5. The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.
      2. All components shall have a custom finish in a color to match a customer supplied sample.
4. Sight-Proof Transfer/Door Grilles – Aluminum Construction [Price Model ATG1/ATGH]:
   1. Construction
      1. Core and frame material shall be aluminum.
   2. Finish shall be (**select one**):
      1. All aluminum components shall have a B15 Aluminum baked-on powder coat finish.
         1. The paint finish must demonstrate no degradation when tested in accordance with ASTM D1308 (covered and spot immersion) and ASTM D4752 (MEK double rub) paint durability tests.
         2. The paint film thickness shall be a minimum of 2.0 mils.
         3. The finish shall have a hardness of 2H.
         4. The finish shall withstand a minimum salt spray exposure of 500 hours with no measurable creep in accordance with ASTM D1654, and 1000 hours of exposure with no rusting or blistering as per ASTM D610 and ASTM D714.
         5. The finish shall have an impact resistance of 80 in/lb.
      2. All aluminum components shall have a custom finish in a color to match a customer supplied sample.
5. Sight-Proof or Light Proof Transfer/Door Grilles – Aluminum Construction [Price Model ATG2]:
   1. Construction
      1. Core and frame material shall be aluminum.
   2. Finish shall be:
      1. All aluminum components shall have a B17 Black baked-on powder coat finish.
         1. The paint finish must demonstrate no degradation when tested in accordance with ASTM D1308 (covered and spot immersion) and ASTM D4752 (MEK double rub) paint durability tests.
         2. The paint film thickness shall be a minimum of 2.0 mils.
         3. The finish shall have a hardness of 2H.
         4. The finish shall withstand a minimum salt spray exposure of 500 hours with no measurable creep in accordance with ASTM D1654, and 1000 hours of exposure with no rusting or blistering as per ASTM D610 and ASTM D714.
         5. The finish shall have an impact resistance of 80 in/lb.
6. Border Styles:
   1. Channel Border:
      1. The grille shall be supplied with a channel border for on-site wood trim framing by others.
   2. Flat border, one side:
      1. The grille shall be supplied with a 1-1/4” wide flat border on one side.
      2. The grille shall include countersunk screw hole fastening.
   3. Flat border, both sides:
      1. The grille shall be supplied with a 1-1/4” wide flat border on both sides.
      2. The grille shall include countersunk screw hole fastening.

**PART 3 – EXECUTION**

**3.01 Examination**

1. Verify that conditions are suitable for installation.
2. Verify that field measurements are as shown on the drawings.

**3.02 Installation**

1. Install in accordance with manufacturer’s instructions.
2. See drawings for the size(s) and locations of grilles.

**3.03 Field Quality Control**

1. See Section 01 40 00 – Quality Requirements for additional requirements.

**3.05 Cleaning**

1. See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

**3.06 Closeout Activities**

1. See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.
2. See Section 01 79 00 – Demonstration and Training for additional requirements.